Cv Calculation Sheet	Page:	1
	No:	1	TAG NO:	FV-3313	CASE:	MAX
Flow rate:	13868	l/h	Fluid state:	FLASH
Inlet Pressure:	25.5	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	air=1	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	3.38	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	3.309
Flash:	5.04	%	Travel:	58	%
	11.56 x 13.17m3/h x Sqr(0.739)
	Cv(Liq)	=	=	2.738
	Sqr(2285kPa)
	339.3m3/h[S] x Sqr(1.25 x 94.8degK)
	Cv(Gas	=	=	0.5708
	2.538 x 2550kPaA
	No:	1	TAG NO:	FV-3313	CASE:	NOR
Flow rate:	13497	l/h	Fluid state:	FLASH
Inlet Pressure:	25.5	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	air=1	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	3.29	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	3.219
Flash:	5.03	%	Travel:	57	%
	11.56 x 12.82m3/h x Sqr(0.739)
	Cv(Liq)	=	=	2.665
	Sqr(2285kPa)
	329.5m3/h[S] x Sqr(1.25 x 94.8degK)
	Cv(Gas	=	=	0.5544
	2.538 x 2550kPaA
	No:	1	TAG NO:	FV-3313	CASE:	MIN
Flow rate:	8711	l/h	Fluid state:	FLASH
Inlet Pressure:	25.5	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	air=1	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.12	m/s
Critical pressure:	barA	S.P.L.:	70	dBA
CP/CV   ,   Z:	Calc. Cv:	2.078
Flash:	5.04	%	Travel:	48	%
	11.56 x 8.272m3/h x Sqr(0.739)
	Cv(Liq)	=	=	1.72
	Sqr(2285kPa)
	213.1m3/h[S] x Sqr(1.25 x 94.8degK)
	Cv(Gas	=	=	0.3585
	2.538 x 2550kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	2
	No:	2	TAG NO:	FV-3314	CASE:	MAX
Flow rate:	17208	l/h	Fluid state:	FLASH
Inlet Pressure:	24.8	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	4.19	m/s
Critical pressure:	barA	S.P.L.:	73	dBA
CP/CV   ,   Z:	Calc. Cv:	4.278
Flash:	5.04	%	Travel:	63	%
	11.56 x 16.34m3/h x Sqr(0.739)
	Cv(Liq)	=	=	3.45
	Sqr(2215kPa)
	544.3m3/h[S] x Sqr(0.9667 x 94.8degK)
	Cv(Gas	=	=	0.8281
	2.538 x 2480kPaA
	No:	2	TAG NO:	FV-3314	CASE:	NOR
Flow rate:	15172	l/h	Fluid state:	FLASH
Inlet Pressure:	24.8	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	3.69	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	3.771
Flash:	5.03	%	Travel:	60	%
	11.56 x 14.41m3/h x Sqr(0.739)
	Cv(Liq)	=	=	3.042
	Sqr(2215kPa)
	478.9m3/h[S] x Sqr(0.9667 x 94.8degK)
	Cv(Gas	=	=	0.7286
	2.538 x 2480kPaA
	No:	2	TAG NO:	FV-3314	CASE:	MIN
Flow rate:	8297	l/h	Fluid state:	FLASH
Inlet Pressure:	24.8	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.02	m/s
Critical pressure:	barA	S.P.L.:	70	dBA
CP/CV   ,   Z:	Calc. Cv:	2.063
Flash:	5.04	%	Travel:	48	%
	11.56 x 7.879m3/h x Sqr(0.739)
	Cv(Liq)	=	=	1.664
	Sqr(2215kPa)
	262.4m3/h[S] x Sqr(0.9667 x 94.8degK)
	Cv(Gas	=	=	0.3993
	2.538 x 2480kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	3
	No:	3	TAG NO:	FV-3331B	CASE:	MAX
Flow rate:	4738	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.33	barA	Model:	AGVM
Outlet pressure:	2.6	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	2	4	inch
Temperature:	11.6	degC	Pipe Sch/ Thick:	10S	3	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.76	Mach
Critical pressure:	barA	S.P.L.:	97	dBA
CP/CV   ,   Z:	Calc. Cv:	11.98
Flash:	5.04	%	Travel:	76	%
	5008m3/h[S] x Sqr(0.9667 x 284.8degK) x 1
	Cv(Gas	=	=	11.98
	2.538 x 2733kPaA
	No:	3	TAG NO:	FV-3331B	CASE:	MIN
Flow rate:	460	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.33	barA	Model:	AGVM
Outlet pressure:	2.6	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	2	4	inch
Temperature:	5.5	degC	Pipe Sch/ Thick:	10S	3	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.07	Mach
Critical pressure:	barA	S.P.L.:	78	dBA
CP/CV   ,   Z:	Calc. Cv:	1.151
Flash:	5.04	%	Travel:	28	%
	486.2m3/h[S] x Sqr(0.9667 x 278.7degK) x 1
	Cv(Gas	=	=	1.151
	2.538 x 2733kPaA
	No:	4	TAG NO:	FV-3350	CASE:	MAX
Flow rate:	2679	l/h	Fluid state:	LIQUID
Inlet Pressure:	25.15	barA	Model:	AGVM
Outlet pressure:	4.19	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	1	1	inch
Temperature:	-144.7	degC	Pipe Sch/ Thick:	10S	2.77	mm
Sp.Gr. (liq.):	0.397	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.83
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.46	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	0.4262
Flash:	%	Travel:	77	%
	11.56 x 2.679m3/h x Sqr(0.397) x 1
	Cv(Liq)	=	=	0.4262
	Sqr(2096kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	4
	No:	4	TAG NO:	FV-3350	CASE:	MIN
Flow rate:	1072	l/h	Fluid state:	LIQUID
Inlet Pressure:	25.15	barA	Model:	AGVM
Outlet pressure:	4.19	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	1	1	inch
Temperature:	-144.7	degC	Pipe Sch/ Thick:	10S	2.77	mm
Sp.Gr. (liq.):	0.397	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.83
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.58	m/s
Critical pressure:	barA	S.P.L.:	68	dBA
CP/CV   ,   Z:	Calc. Cv:	0.1706
Flash:	%	Travel:	53	%
	11.56 x 1.072m3/h x Sqr(0.397) x 1
	Cv(Liq)	=	=	0.1706
	Sqr(2096kPa)
	No:	5	TAG NO:	FV-3401	CASE:	MAX
Flow rate:	28343	l/h	Fluid state:	LIQUID
Inlet Pressure:	24.7	barA	Model:	AGVM
Outlet pressure:	24.43	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.455	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.01
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.72	m/s
Critical pressure:	barA	S.P.L.:	49	dBA
CP/CV   ,   Z:	Calc. Cv:	42.53
Flash:	%	Travel:	67	%
	11.56 x 28.34m3/h x Sqr(0.455) x 1
	Cv(Liq)	=	=	42.53
	Sqr(27kPa)
	No:	5	TAG NO:	FV-3401	CASE:	NOR
Flow rate:	27477	l/h	Fluid state:	LIQUID
Inlet Pressure:	24.7	barA	Model:	AGVM
Outlet pressure:	24.43	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.455	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.01
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.67	m/s
Critical pressure:	barA	S.P.L.:	49	dBA
CP/CV   ,   Z:	Calc. Cv:	41.23
Flash:	%	Travel:	66	%
	11.56 x 27.48m3/h x Sqr(0.455) x 1
	Cv(Liq)	=	=	41.23
	Sqr(27kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	5
	No:	5	TAG NO:	FV-3401	CASE:	MIN
Flow rate:	19840	l/h	Fluid state:	LIQUID
Inlet Pressure:	24.7	barA	Model:	AGVM
Outlet pressure:	24.43	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.455	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.01
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.2	m/s
Critical pressure:	barA	S.P.L.:	47	dBA
CP/CV   ,   Z:	Calc. Cv:	29.77
Flash:	%	Travel:	60	%
	11.56 x 19.84m3/h x Sqr(0.455) x 1
	Cv(Liq)	=	=	29.77
	Sqr(27kPa)
	No:	6	TAG NO:	FV-3503	CASE:	MAX
Flow rate:	2064	l/h	Fluid state:	FLASH
Inlet Pressure:	25	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	1-1/2	1-1/2	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	2.77	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.13	m/s
Critical pressure:	barA	S.P.L.:	65	dBA
CP/CV   ,   Z:	Calc. Cv:	0.4812
Flash:	3.15	%	Travel:	56	%
	11.56 x 1.999m3/h x Sqr(0.739)
	Cv(Liq)	=	=	0.4202
	Sqr(2235kPa)
	40.8m3/h[S] x Sqr(0.9667 x 93.1degK)
	Cv(Gas	=	=	0.06103
	2.538 x 2500kPaA
	No:	6	TAG NO:	FV-3503	CASE:	MIN
Flow rate:	1274	l/h	Fluid state:	FLASH
Inlet Pressure:	25	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	1-1/2	1-1/2	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	2.77	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.69	m/s
Critical pressure:	barA	S.P.L.:	64	dBA
CP/CV   ,   Z:	Calc. Cv:	0.2971
Flash:	3.16	%	Travel:	43	%
	11.56 x 1.234m3/h x Sqr(0.739)
	Cv(Liq)	=	=	0.2593
	Sqr(2235kPa)
	25.27m3/h[S] x Sqr(0.9667 x 93.1degK)
	Cv(Gas	=	=	0.03779
	2.538 x 2500kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	6
	No:	7	TAG NO:	FV-3535	CASE:	MAX
Flow rate:	11833	l/h	Fluid state:	LIQUID
Inlet Pressure:	3.17	barA	Model:	AGVM
Outlet pressure:	3.05	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-182.2	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.04
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.62	m/s
Critical pressure:	barA	S.P.L.:	48	dBA
CP/CV   ,   Z:	Calc. Cv:	33.95
Flash:	%	Travel:	80	%
	11.56 x 11.83m3/h x Sqr(0.739) x 1
	Cv(Liq)	=	=	33.95
	Sqr(12kPa)
	No:	7	TAG NO:	FV-3535	CASE:	NOR
Flow rate:	10370	l/h	Fluid state:	LIQUID
Inlet Pressure:	3.24	barA	Model:	AGVM
Outlet pressure:	3.05	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-182.2	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.06
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.42	m/s
Critical pressure:	barA	S.P.L.:	49	dBA
CP/CV   ,   Z:	Calc. Cv:	23.64
Flash:	%	Travel:	72	%
	11.56 x 10.37m3/h x Sqr(0.739) x 1
	Cv(Liq)	=	=	23.64
	Sqr(19kPa)
	No:	7	TAG NO:	FV-3535	CASE:	MIN
Flow rate:	7575	l/h	Fluid state:	LIQUID
Inlet Pressure:	3.24	barA	Model:	AGVM
Outlet pressure:	3.05	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-182.2	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.06
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.03	m/s
Critical pressure:	barA	S.P.L.:	48	dBA
CP/CV   ,   Z:	Calc. Cv:	17.27
Flash:	%	Travel:	66	%
	11.56 x 7.575m3/h x Sqr(0.739) x 1
	Cv(Liq)	=	=	17.27
	Sqr(19kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	7
	No:	8	TAG NO:	FV-3560	CASE:	MAX
Flow rate:	14536	l/h	Fluid state:	LIQUID
Inlet Pressure:	2.71	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-148.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.403	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.02
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.88	m/s
Critical pressure:	barA	S.P.L.:	45	dBA
CP/CV   ,   Z:	Calc. Cv:	43.55
Flash:	%	Travel:	68	%
	11.56 x 14.54m3/h x Sqr(0.403) x 1
	Cv(Liq)	=	=	43.55
	Sqr(6kPa)
	No:	8	TAG NO:	FV-3560	CASE:	NOR
Flow rate:	9676	l/h	Fluid state:	LIQUID
Inlet Pressure:	2.73	barA	Model:	AGVM
Outlet pressure:	2.63	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-148.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.403	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.04
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.58	m/s
Critical pressure:	barA	S.P.L.:	45	dBA
CP/CV   ,   Z:	Calc. Cv:	22.45
Flash:	%	Travel:	54	%
	11.56 x 9.676m3/h x Sqr(0.403) x 1
	Cv(Liq)	=	=	22.45
	Sqr(10kPa)
	No:	8	TAG NO:	FV-3560	CASE:	MIN
Flow rate:	2225	l/h	Fluid state:	LIQUID
Inlet Pressure:	2.79	barA	Model:	AGVM
Outlet pressure:	2.67	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-148.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.403	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.04
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.13	m/s
Critical pressure:	barA	S.P.L.:	40	dBA
CP/CV   ,   Z:	Calc. Cv:	4.714
Flash:	%	Travel:	22	%
	11.56 x 2.225m3/h x Sqr(0.403) x 1
	Cv(Liq)	=	=	4.714
	Sqr(12kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	8
	No:	9	TAG NO:	FV-3715	CASE:	NOR
Flow rate:	15323	l/h	Fluid state:	LIQUID
Inlet Pressure:	25.53	barA	Model:	AGVM
Outlet pressure:	2.68	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	4	4	inch
Temperature:	-144.7	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.554	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.1	m/s
Critical pressure:	barA	S.P.L.:	81	dBA
CP/CV   ,   Z:	Calc. Cv:	2.758
Flash:	%	Travel:	56	%
	11.56 x 15.32m3/h x Sqr(0.554) x 1
	Cv(Liq)	=	=	2.758
	Sqr(2285kPa)
	No:	10	TAG NO:	FV-3725	CASE:	NOR
Flow rate:	15323	l/h	Fluid state:	LIQUID
Inlet Pressure:	25.53	barA	Model:	AGVM
Outlet pressure:	2.68	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	4	4	inch
Temperature:	-144.7	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.554	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.1	m/s
Critical pressure:	barA	S.P.L.:	81	dBA
CP/CV   ,   Z:	Calc. Cv:	2.758
Flash:	%	Travel:	56	%
	11.56 x 15.32m3/h x Sqr(0.554) x 1
	Cv(Liq)	=	=	2.758
	Sqr(2285kPa)
	No:	11	TAG NO:	FV-3883	CASE:	MAX
Flow rate:	13614	l/h	Fluid state:	FLASH
Inlet Pressure:	25.4	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	3.31	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	3.143
Flash:	3.15	%	Travel:	64	%
	11.56 x 13.19m3/h x Sqr(0.739)
	Cv(Liq)	=	=	2.747
	Sqr(2275kPa)
	269.1m3/h[S] x Sqr(0.9667 x 93.1degK)
	Cv(Gas	=	=	0.3962
	2.538 x 2540kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	9
	No:	11	TAG NO:	FV-3883	CASE:	MIN
Flow rate:	10246	l/h	Fluid state:	FLASH
Inlet Pressure:	25.4	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.49	m/s
Critical pressure:	barA	S.P.L.:	71	dBA
CP/CV   ,   Z:	Calc. Cv:	2.366
Flash:	3.16	%	Travel:	58	%
	11.56 x 9.922m3/h x Sqr(0.739)
	Cv(Liq)	=	=	2.067
	Sqr(2275kPa)
	203.2m3/h[S] x Sqr(0.9667 x 93.1degK)
	Cv(Gas	=	=	0.2991
	2.538 x 2540kPaA
	No:	12	TAG NO:	HV-3381	CASE:	MAX
Flow rate:	6000	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.07	barA	Model:	AGVM
Outlet pressure:	2.85	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	inch
Temperature:	-139.5	degC	Pipe Sch/ Thick:	10S	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.6	Mach
Critical pressure:	barA	S.P.L.:	dBA
CP/CV   ,   Z:	Calc. Cv:	10.49
Flash:	3.15	%	Travel:	73	%
	6342m3/h[S] x Sqr(0.9667 x 133.7degK) x 1
	Cv(Gas	=	=	10.49
	2.538 x 2707kPaA
	No:	12	TAG NO:	HV-3381	CASE:	NOR
Flow rate:	3000	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.07	barA	Model:	AGVM
Outlet pressure:	2.85	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	inch
Temperature:	-139.5	degC	Pipe Sch/ Thick:	10S	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.3	Mach
Critical pressure:	barA	S.P.L.:	dBA
CP/CV   ,   Z:	Calc. Cv:	5.246
Flash:	%	Travel:	59	%
	3171m3/h[S] x Sqr(0.9667 x 133.7degK) x 1
	Cv(Gas	=	=	5.246
	2.538 x 2707kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	10
	No:	12	TAG NO:	HV-3381	CASE:	MIN
Flow rate:	900	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.07	barA	Model:	AGVM
Outlet pressure:	2.85	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	inch
Temperature:	-139.5	degC	Pipe Sch/ Thick:	10S	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.89
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.09	Mach
Critical pressure:	barA	S.P.L.:	dBA
CP/CV   ,   Z:	Calc. Cv:	1.574
Flash:	%	Travel:	34	%
	951.3m3/h[S] x Sqr(0.9667 x 133.7degK) x 1
	Cv(Gas	=	=	1.574
	2.538 x 2707kPaA
	No:	13	TAG NO:	HV-3428	CASE:	MAX
Flow rate:	8062	l/h	Fluid state:	FLASH
Inlet Pressure:	23.85	barA	Model:	AGVM
Outlet pressure:	8.11	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	1-1/2	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	2.77	mm
Sp.Gr. (liq.):	0.627	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1	kg/m3[N]	KC:	0.66
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.96	m/s
Critical pressure:	barA	S.P.L.:	67	dBA
CP/CV   ,   Z:	Calc. Cv:	2.032
Flash:	3.04	%	Travel:	48	%
	11.56 x 7.817m3/h x Sqr(0.627)
	Cv(Liq)	=	=	1.804
	Sqr(1574kPa)
	163.1m3/h[S] x Sqr(0.7734 x 93.1degK)
	Cv(Gas	=	=	0.2287
	2.538 x 2385kPaA
	No:	13	TAG NO:	HV-3428	CASE:	MIN
Flow rate:	1613	l/h	Fluid state:	FLASH
Inlet Pressure:	23.85	barA	Model:	AGVM
Outlet pressure:	8.11	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	3	1-1/2	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	2.77	mm
Sp.Gr. (liq.):	0.629	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1	kg/m3[N]	KC:	0.66
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.39	m/s
Critical pressure:	barA	S.P.L.:	62	dBA
CP/CV   ,   Z:	Calc. Cv:	0.4134
Flash:	3.57	%	Travel:	15	%
	11.56 x 1.555m3/h x Sqr(0.629)
	Cv(Liq)	=	=	0.3594
	Sqr(1574kPa)
	38.45m3/h[S] x Sqr(0.7734 x 93.1degK)
	Cv(Gas	=	=	0.05391
	2.538 x 2385kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	11
	No:	14	TAG NO:	HV-3540	CASE:	NOR
Flow rate:	9578	l/h	Fluid state:	FLASH
Inlet Pressure:	5.5	barA	Model:	AGVM
Outlet pressure:	4.2	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	1-1/2	1-1/2	inch
Temperature:	-178	degC	Pipe Sch/ Thick:	10S	2.77	mm
Sp.Gr. (liq.):	0.718	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.24
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.33	m/s
Critical pressure:	barA	S.P.L.:	52	dBA
CP/CV   ,   Z:	Calc. Cv:	12.79
Flash:	10	%	Travel:	70	%
	11.56 x 8.62m3/h x Sqr(0.718)
	Cv(Liq)	=	=	7.406
	Sqr(130kPa)
	584m3/h[S] x Sqr(0.9667 x 95.1degK)
	Cv(Gas	=	=	5.384
	2.930 x Sqr(130kPa x (550kPaA + 420kPaA))
	No:	15	TAG NO:	LV-3316	CASE:	MAX
Flow rate:	31890	l/h	Fluid state:	LIQUID
Inlet Pressure:	3.73	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	6	inch
Temperature:	-182.2	degC	Pipe Sch/ Thick:	10S	3.4	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.29
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.94	m/s
Critical pressure:	barA	S.P.L.:	61	dBA
CP/CV   ,   Z:	Calc. Cv:	30.49
Flash:	%	Travel:	66	%
	11.56 x 31.89m3/h x Sqr(0.739) x 1
	Cv(Liq)	=	=	30.49
	Sqr(108kPa)
	No:	15	TAG NO:	LV-3316	CASE:	NOR
Flow rate:	29760	l/h	Fluid state:	LIQUID
Inlet Pressure:	3.73	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	6	inch
Temperature:	-182.2	degC	Pipe Sch/ Thick:	10S	3.4	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.29
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.81	m/s
Critical pressure:	barA	S.P.L.:	61	dBA
CP/CV   ,   Z:	Calc. Cv:	28.46
Flash:	%	Travel:	65	%
	11.56 x 29.76m3/h x Sqr(0.739) x 1
	Cv(Liq)	=	=	28.46
	Sqr(108kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	12
	No:	15	TAG NO:	LV-3316	CASE:	MIN
Flow rate:	18331	l/h	Fluid state:	LIQUID
Inlet Pressure:	3.73	barA	Model:	AGVM
Outlet pressure:	2.36	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	6	inch
Temperature:	-182.2	degC	Pipe Sch/ Thick:	10S	3.4	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.37
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.11	m/s
Critical pressure:	barA	S.P.L.:	61	dBA
CP/CV   ,   Z:	Calc. Cv:	15.56
Flash:	%	Travel:	53	%
	11.56 x 18.33m3/h x Sqr(0.739) x 1
	Cv(Liq)	=	=	15.56
	Sqr(137kPa)
	No:	16	TAG NO:	LV-3420	CASE:	MAX
Flow rate:	32932	l/h	Fluid state:	FLASH
Inlet Pressure:	23.85	barA	Model:	AGVM
Outlet pressure:	10.82	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.626	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1	kg/m3[N]	KC:	0.55
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2	m/s
Critical pressure:	barA	S.P.L.:	71	dBA
CP/CV   ,   Z:	Calc. Cv:	9.01
Flash:	2.98	%	Travel:	52	%
	11.56 x 31.95m3/h x Sqr(0.626)
	Cv(Liq)	=	=	8.096
	Sqr(1303kPa)
	652.2m3/h[S] x Sqr(0.7734 x 93.1degK)
	Cv(Gas	=	=	0.9145
	2.538 x 2385kPaA
	No:	16	TAG NO:	LV-3420	CASE:	NOR
Flow rate:	26485	l/h	Fluid state:	FLASH
Inlet Pressure:	23.86	barA	Model:	AGVM
Outlet pressure:	9.42	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.613	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.98	kg/m3[N]	KC:	0.61
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.61	m/s
Critical pressure:	barA	S.P.L.:	71	dBA
CP/CV   ,   Z:	Calc. Cv:	6.829
Flash:	2.88	%	Travel:	46	%
	11.56 x 25.72m3/h x Sqr(0.613)
	Cv(Liq)	=	=	6.127
	Sqr(1444kPa)
	506.5m3/h[S] x Sqr(0.7579 x 93.1degK)
	Cv(Gas	=	=	0.7028
	2.538 x 2386kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	13
	No:	16	TAG NO:	LV-3420	CASE:	MIN
Flow rate:	6571	l/h	Fluid state:	FLASH
Inlet Pressure:	23.85	barA	Model:	AGVM
Outlet pressure:	7.22	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.630	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1	kg/m3[N]	KC:	0.7
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.4	m/s
Critical pressure:	barA	S.P.L.:	67	dBA
CP/CV   ,   Z:	Calc. Cv:	1.642
Flash:	3.5	%	Travel:	17	%
	11.56 x 6.341m3/h x Sqr(0.63)
	Cv(Liq)	=	=	1.427
	Sqr(1663kPa)
	153.8m3/h[S] x Sqr(0.7734 x 93.1degK)
	Cv(Gas	=	=	0.2157
	2.538 x 2385kPaA
	No:	17	TAG NO:	LV-3421	CASE:	MAX
Flow rate:	40971	l/h	Fluid state:	FLASH
Inlet Pressure:	24.11	barA	Model:	AGVM
Outlet pressure:	10.18	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	4	inch
Temperature:	-177.1	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.536	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.85	kg/m3[N]	KC:	0.58
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.49	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	9.864
Flash:	2.18	%	Travel:	54	%
	11.56 x 40.08m3/h x Sqr(0.536)
	Cv(Liq)	=	=	9.088
	Sqr(1393kPa)
	597.9m3/h[S] x Sqr(0.6574 x 96degK)
	Cv(Gas	=	=	0.7764
	2.538 x 2411kPaA
	No:	17	TAG NO:	LV-3421	CASE:	NOR
Flow rate:	40382	l/h	Fluid state:	FLASH
Inlet Pressure:	24.11	barA	Model:	AGVM
Outlet pressure:	9.18	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	4	inch
Temperature:	-176.9	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.539	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.86	kg/m3[N]	KC:	0.62
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.46	m/s
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	9.458
Flash:	2.24	%	Travel:	53	%
	11.56 x 39.48m3/h x Sqr(0.539)
	Cv(Liq)	=	=	8.671
	Sqr(1493kPa)
	601.8m3/h[S] x Sqr(0.6651 x 96.3degK)
	Cv(Gas	=	=	0.7869
	2.538 x 2411kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	14
	No:	17	TAG NO:	LV-3421	CASE:	MIN
Flow rate:	26422	l/h	Fluid state:	FLASH
Inlet Pressure:	24.13	barA	Model:	AGVM
Outlet pressure:	6.97	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	4	inch
Temperature:	-174.8	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.51	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.82	kg/m3[N]	KC:	0.71
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.61	m/s
Critical pressure:	barA	S.P.L.:	71	dBA
CP/CV   ,   Z:	Calc. Cv:	5.66
Flash:	2.29	%	Travel:	43	%
	11.56 x 25.82m3/h x Sqr(0.51)
	Cv(Liq)	=	=	5.145
	Sqr(1716kPa)
	399.5m3/h[S] x Sqr(0.6342 x 98.3degK)
	Cv(Gas	=	=	0.5152
	2.538 x 2413kPaA
	No:	18	TAG NO:	LV-3422	CASE:	MAX
Flow rate:	7829	l/h	Fluid state:	FLASH
Inlet Pressure:	25.6	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	2	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.966	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.9	m/s
Critical pressure:	barA	S.P.L.:	70	dBA
CP/CV   ,   Z:	Calc. Cv:	1.957
Flash:	5.04	%	Travel:	54	%
	11.56 x 7.434m3/h x Sqr(0.739)
	Cv(Liq)	=	=	1.542
	Sqr(2295kPa)
	320.4m3/h[S] x Sqr(0.7471 x 94.8degK)
	Cv(Gas	=	=	0.4152
	2.538 x 2560kPaA
	No:	18	TAG NO:	LV-3422	CASE:	NOR
Flow rate:	7974	l/h	Fluid state:	FLASH
Inlet Pressure:	25.6	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	2	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.966	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.94	m/s
Critical pressure:	barA	S.P.L.:	70	dBA
CP/CV   ,   Z:	Calc. Cv:	1.993
Flash:	5.03	%	Travel:	54	%
	11.56 x 7.573m3/h x Sqr(0.739)
	Cv(Liq)	=	=	1.571
	Sqr(2295kPa)
	325.7m3/h[S] x Sqr(0.7471 x 94.8degK)
	Cv(Gas	=	=	0.422
	2.538 x 2560kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	15
	No:	18	TAG NO:	LV-3422	CASE:	MIN
Flow rate:	3733	l/h	Fluid state:	FLASH
Inlet Pressure:	25.6	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	2	3	inch
Temperature:	-178.3	degC	Pipe Sch/ Thick:	10S	3.05	mm
Sp.Gr. (liq.):	0.739	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.966	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.91	m/s
Critical pressure:	barA	S.P.L.:	68	dBA
CP/CV   ,   Z:	Calc. Cv:	0.9333
Flash:	5.04	%	Travel:	39	%
	11.56 x 3.545m3/h x Sqr(0.739)
	Cv(Liq)	=	=	0.7353
	Sqr(2295kPa)
	152.8m3/h[S] x Sqr(0.7471 x 94.8degK)
	Cv(Gas	=	=	0.198
	2.538 x 2560kPaA
	No:	19	TAG NO:	LV-3423A	CASE:	MAX
Flow rate:	44056	l/h	Fluid state:	LIQUID
Inlet Pressure:	7.1	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	6	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.4	mm
Sp.Gr. (liq.):	0.572	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.63
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.68	m/s
Critical pressure:	barA	S.P.L.:	80	dBA
CP/CV   ,   Z:	Calc. Cv:	18.26
Flash:	%	Travel:	67	%
	11.56 x 44.06m3/h x Sqr(0.572) x 1
	Cv(Liq)	=	=	18.26
	Sqr(445kPa)
	No:	19	TAG NO:	LV-3423A	CASE:	NOR
Flow rate:	41845	l/h	Fluid state:	LIQUID
Inlet Pressure:	8.09	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	6	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.4	mm
Sp.Gr. (liq.):	0.577	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.67
Viscosity:	cP
Vapor pressure:	barA	Velocity:	2.55	m/s
Critical pressure:	barA	S.P.L.:	81	dBA
CP/CV   ,   Z:	Calc. Cv:	15.75
Flash:	%	Travel:	64	%
	11.56 x 41.85m3/h x Sqr(0.577) x 1
	Cv(Liq)	=	=	15.75
	Sqr(544kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	16
	No:	19	TAG NO:	LV-3423A	CASE:	MIN
Flow rate:	22339	l/h	Fluid state:	LIQUID
Inlet Pressure:	7.94	barA	Model:	AGVM
Outlet pressure:	2.65	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	6	6	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.4	mm
Sp.Gr. (liq.):	0.55	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.67
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.36	m/s
Critical pressure:	barA	S.P.L.:	78	dBA
CP/CV   ,   Z:	Calc. Cv:	8.327
Flash:	%	Travel:	51	%
	11.56 x 22.34m3/h x Sqr(0.55) x 1
	Cv(Liq)	=	=	8.327
	Sqr(529kPa)
	No:	20	TAG NO:	LV-3423B	CASE:	MAX
Flow rate:	27190	l/h	Fluid state:	LIQUID
Inlet Pressure:	7.99	barA	Model:	AGVM
Outlet pressure:	2.8	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.594	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.65
Viscosity:	cP
Vapor pressure:	barA	Velocity:	3.72	m/s
Critical pressure:	barA	S.P.L.:	79	dBA
CP/CV   ,   Z:	Calc. Cv:	10.63
Flash:	%	Travel:	66	%
	11.56 x 27.19m3/h x Sqr(0.594) x 1
	Cv(Liq)	=	=	10.63
	Sqr(519kPa)
	No:	20	TAG NO:	LV-3423B	CASE:	NOR
Flow rate:	22583	l/h	Fluid state:	LIQUID
Inlet Pressure:	8.6	barA	Model:	AGVM
Outlet pressure:	2.8	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.577	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.67
Viscosity:	cP
Vapor pressure:	barA	Velocity:	3.09	m/s
Critical pressure:	barA	S.P.L.:	78	dBA
CP/CV   ,   Z:	Calc. Cv:	8.234
Flash:	%	Travel:	61	%
	11.56 x 22.58m3/h x Sqr(0.577) x 1
	Cv(Liq)	=	=	8.234
	Sqr(580kPa)
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	17
	No:	20	TAG NO:	LV-3423B	CASE:	MIN
Flow rate:	10794	l/h	Fluid state:	LIQUID
Inlet Pressure:	8.42	barA	Model:	AGVM
Outlet pressure:	2.8	barA	Valve size:	2	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-180	degC	Pipe Sch/ Thick:	3.05	mm
Sp.Gr. (liq.):	0.55	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	kg/m3[N]	KC:	0.67
Viscosity:	cP
Vapor pressure:	barA	Velocity:	1.48	m/s
Critical pressure:	barA	S.P.L.:	75	dBA
CP/CV   ,   Z:	Calc. Cv:	3.903
Flash:	%	Travel:	45	%
	11.56 x 10.79m3/h x Sqr(0.55) x 1
	Cv(Liq)	=	=	3.903
	Sqr(562kPa)
	No:	21	TAG NO:	PV-3406A	CASE:	MAX
Flow rate:	1680	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	8.5	barA	Model:	AGVM
Outlet pressure:	2.71	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	2	2	inch
Temperature:	-176.5	degC	Pipe Sch/ Thick:	2.77	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.35	kg/m3[N]	KC:	0.68
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.32	Mach
Critical pressure:	barA	S.P.L.:	70	dBA
CP/CV   ,   Z:	Calc. Cv:	4.21
Flash:	%	Travel:	77	%
	1776m3/h[S] x Sqr(0.2707 x 96.6degK) x 1
	Cv(Gas	=	=	4.21
	2.538 x 850kPaA
	No:	21	TAG NO:	PV-3406A	CASE:	NOR
Flow rate:	1509	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	9.1	barA	Model:	AGVM
Outlet pressure:	2.71	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	2	2	inch
Temperature:	-176.5	degC	Pipe Sch/ Thick:	2.77	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.34	kg/m3[N]	KC:	0.7
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.28	Mach
Critical pressure:	barA	S.P.L.:	69	dBA
CP/CV   ,   Z:	Calc. Cv:	3.482
Flash:	%	Travel:	72	%
	1595m3/h[S] x Sqr(0.263 x 96.6degK) x 1
	Cv(Gas	=	=	3.482
	2.538 x 910kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	18
	No:	21	TAG NO:	PV-3406A	CASE:	MIN
Flow rate:	741	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	8.9	barA	Model:	AGVM
Outlet pressure:	2.71	barA	Valve size:	1	inch
Diff. pressure	bar	Line size  	2	2	inch
Temperature:	-174.3	degC	Pipe Sch/ Thick:	2.77	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.35	kg/m3[N]	KC:	0.7
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.14	Mach
Critical pressure:	barA	S.P.L.:	63	dBA
CP/CV   ,   Z:	Calc. Cv:	1.794
Flash:	%	Travel:	54	%
	783.2m3/h[S] x Sqr(0.2707 x 98.8degK) x 1
	Cv(Gas	=	=	1.794
	2.538 x 890kPaA
	No:	22	TAG NO:	PV-3406B	CASE:	NOR
Flow rate:	15593	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	12	barA	Model:	AGVM
Outlet pressure:	1.2	barA	Valve size:	4	inch
Diff. pressure	bar	Line size  	4	6	inch
Temperature:	-166.6	degC	Pipe Sch/ Thick:	3.4	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.9
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.83	Mach
Critical pressure:	barA	S.P.L.:	104	dBA
CP/CV   ,   Z:	Calc. Cv:	54.92
Flash:	%	Travel:	61	%
	16482m3/h[S] x Sqr(0.9667 x 106.5degK) x 1
	Cv(Gas	=	=	54.92
	2.538 x 1200kPaA
	No:	23	TAG NO:	PV-3531A	CASE:	MAX
Flow rate:	16899	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	4	barA	Model:	HTS
Outlet pressure:	1.2	barA	Valve size:	6	inch
Diff. pressure	bar	Line size  	6	10	inch
Temperature:	-150	degC	Pipe Sch/ Thick:	10S	4	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.96	kg/m3[N]	KC:	0.7
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.38	Mach
Critical pressure:	barA	S.P.L.:	102	dBA
CP/CV   ,   Z:	Calc. Cv:	168.2
Flash:	%	Travel:	83	%
	17862m3/h[S] x Sqr(0.7425 x 123.1degK) x 1
	Cv(Gas	=	=	168.2
	2.538 x 400kPaA
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	19
	No:	23	TAG NO:	PV-3531A	CASE:	NOR
Flow rate:	14088	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	4	barA	Model:	HTS
Outlet pressure:	1.2	barA	Valve size:	6	inch
Diff. pressure	bar	Line size  	6	10	inch
Temperature:	-150	degC	Pipe Sch/ Thick:	10S	4	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.93	kg/m3[N]	KC:	0.7
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.31	Mach
Critical pressure:	barA	S.P.L.:	100	dBA
CP/CV   ,   Z:	Calc. Cv:	138
Flash:	%	Travel:	76	%
	14891m3/h[S] x Sqr(0.7193 x 123.1degK) x 1
	Cv(Gas	=	=	138
	2.538 x 400kPaA
	No:	23	TAG NO:	PV-3531A	CASE:	MIN
Flow rate:	6765	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	4	barA	Model:	HTS
Outlet pressure:	1.2	barA	Valve size:	6	inch
Diff. pressure	bar	Line size  	6	10	inch
Temperature:	-150	degC	Pipe Sch/ Thick:	10S	4	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	0.88	kg/m3[N]	KC:	0.7
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.14	Mach
Critical pressure:	barA	S.P.L.:	94	dBA
CP/CV   ,   Z:	Calc. Cv:	64.48
Flash:	%	Travel:	55	%
	7151m3/h[S] x Sqr(0.6806 x 123.1degK) x 1
	Cv(Gas	=	=	64.48
	2.538 x 400kPaA
	No:	24	TAG NO:	SV-3640	CASE:	MAX
Flow rate:	4738	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.33	barA	Model:	HTS
Outlet pressure:	27.14	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	11.6	degC	Pipe Sch/ Thick:	10S	3	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.01
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.03	Mach
Critical pressure:	barA	S.P.L.:	59	dBA
CP/CV   ,   Z:	Calc. Cv:	88.15
Flash:	%	Travel:	81	%
	5008m3/h[S] x Sqr(0.9667 x 284.8degK) x 1
	Cv(Gas	=	=	88.15
	2.930 x Sqr(19kPa x (2733kPaA + 2714kPaA))
419: Air Liquide France (Rev.1)/ 

	Cv Calculation Sheet	Page:	20
	No:	24	TAG NO:	SV-3640	CASE:	NOR
Flow rate:	3635	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.33	barA	Model:	HTS
Outlet pressure:	20.26	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	-5.8	degC	Pipe Sch/ Thick:	10S	3	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.26
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.03	Mach
Critical pressure:	barA	S.P.L.:	74	dBA
CP/CV   ,   Z:	Calc. Cv:	11.49
Flash:	%	Travel:	25	%
	3842m3/h[S] x Sqr(0.9667 x 267.3degK) x 1
	Cv(Gas	=	=	11.49
	2.930 x Sqr(707kPa x (2733kPaA + 2026kPaA))
	No:	24	TAG NO:	SV-3640	CASE:	MIN
Flow rate:	2850	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	27.33	barA	Model:	HTS
Outlet pressure:	16.2	barA	Valve size:	3	inch
Diff. pressure	bar	Line size  	3	3	inch
Temperature:	5.5	degC	Pipe Sch/ Thick:	10S	3	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.41
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.03	Mach
Critical pressure:	barA	S.P.L.:	78	dBA
CP/CV   ,   Z:	Calc. Cv:	7.666
Flash:	%	Travel:	20	%
	3012m3/h[S] x Sqr(0.9667 x 278.7degK) x 1
	Cv(Gas	=	=	7.666
	2.930 x Sqr(1113kPa x (2733kPaA + 1620kPaA))
	No:	25	TAG NO:	TDV-3510	CASE:	MAX
Flow rate:	1400	m3/h[N]	Fluid state:	GAS
Inlet Pressure:	5.5	barA	Model:	HTS
Outlet pressure:	1.27	barA	Valve size:	1-1/2	inch
Diff. pressure	bar	Line size  	1-1/2	1-1/2	inch
Temperature:	-178	degC	Pipe Sch/ Thick:	10S	2.8	mm
Sp.Gr. (liq.):	water=1	Saturated temp.:	degC
Sp.Gr. (gas,vapor):	1.25	kg/m3[N]	KC:	0.77
Viscosity:	cP
Vapor pressure:	barA	Velocity:	0.47	Mach
Critical pressure:	barA	S.P.L.:	72	dBA
CP/CV   ,   Z:	Calc. Cv:	10.17
Flash:	%	Travel:	82	%
	1480m3/h[S] x Sqr(0.9667 x 95.1degK) x 1
	Cv(Gas	=	=	10.17
	2.538 x 550kPaA
419: Air Liquide France (Rev.1)/