Specification Sheet	Page:	1
 No.:	1	QTY:	1	 Product no.:
 Tag no.	FV-3313
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1	inch	Scope: valve body and bonnet
   Rated Cv	14
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	HPCOL-5fromE307toV304	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	13868	13497	8711	l/h	<Note>	Tokumi	V93-9618-	-	53
   Inlet pressure	25.5	25.5	25.5	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.65	2.65	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	34	bar	Welded disk
   Temperature	-178.3	-178.3	-178.3	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	0.739	water=1
   	1.25	1.25	1.25	air=1
   Viscosity	cP
   Flash	5.04	5.03	5.04	%	<Line spec>
	Design press.	34	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	3.309	3.219	2.078	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	2
 No.:	2	QTY:	1	 Product no.:
 Tag no.	FV-3314
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1	inch	Scope: valve body and bonnet
   Rated Cv	14
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	HPCOL-4fromE306toV304	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	17208	15172	8297	l/h	<Note>	Tokumi	V93-9618-	-	54
   Inlet pressure	24.8	24.8	24.8	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.65	2.65	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	34	bar	Welded disk
   Temperature	-178.3	-178.3	-178.3	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	0.739	water=1
   	1.25	1.25	1.25	kg/m3[N]
   Viscosity	cP
   Flash	5.04	5.03	5.04	%	<Line spec>
	Design press.	34	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	4.278	3.771	2.063	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	3
 No.:	3	QTY:	1	 Product no.:
 Tag no.	FV-3331B
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/2	inch	Scope: valve body and bonnet
   Rated Cv	21
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA4	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	ET-301 bypass	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	4738	460	m3/h[N]	<Note>	Tokumi	V93-9618-	-	55
   Inlet pressure	27.33	27.33	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.6	2.6	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	34	bar	Welded disk
   Temperature	11.6	5.5	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	water=1
   	1.25	1.25	kg/m3[N]
   Viscosity	cP
   Flash	5.04	5.04	%	<Line spec>
	Design press.	34	barG
	Design temp.	5.5~65	degC
   Calculated Cv	11.98	1.151	 	Line size  in/out	2	4	inch
	Line Sch. / Thick.	10S	3	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	4
 No.:	4	QTY:	1	 Product no.:
 Tag no.	FV-3350
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3/4	inch	  SV0801-E01    Material certificate in english. 
	   Port size	Cv=1.0	inch	Scope: valve body and bonnet
   Rated Cv	1.0
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA1	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	Excess CH4toE-301(Fuelgas 	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	2679	1072	l/h	<Note>	Tokumi	V93-9618-	-	56
   Inlet pressure	25.15	25.15	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	4.19	4.19	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	39	bar	Welded disk
   Temperature	-144.7	-144.7	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.397	0.397	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	39	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	0.4262	0.1706	 	Line size  in/out	1	1	inch
	Line Sch. / Thick.	10S	2.77	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	5
 No.:	5	QTY:	1	 Product no.:
 Tag no.	FV-3401
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2	inch	Scope: valve body and bonnet
   Rated Cv	50
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA6	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	4.0bar
   Spring range	2.0-3.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD3D-1CYL-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	CH4 wash to K301	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	28343	27477	19840	l/h	<Note>	Tokumi	V93-9618-	-	57
   Inlet pressure	24.7	24.7	24.7	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	24.43	24.43	24.43	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	39	bar
   Temperature	-180	-180	-180	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.455	0.455	0.455	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	39	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	42.53	41.23	29.77	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	6
 No.:	6	QTY:	1	 Product no.:
 Tag no.	FV-3503
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3/4	inch	  SV0801-E01    Material certificate in english. 
	   Port size	Cv=2.5	inch	Scope: valve body and bonnet
   Rated Cv	2.5
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA1	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	HPCOfromE304toV304	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	2064	1274	l/h	<Note>	Tokumi	V93-9618-	-	58
   Inlet pressure	25	25	barA	start up CV=1.5
   Outlet pressure	2.65	2.65	barA	Air piping: Stainless steel (316ss)
   Diff. pressure	bar	Swagelock double ferules
   Shut-off press.	34	bar	with Diffuser
   Temperature	-180	-180	degC	Welded disk,    STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	water=1
   	1.25	1.25	kg/m3[N]
   Viscosity	cP
   Flash	3.15	3.16	%	<Line spec>
	Design press.	34	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	0.4812	0.2971	 	Line size  in/out	1-1/2	1-1/2	inch
	Line Sch. / Thick.	10S	2.77	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	7
 No.:	7	QTY:	1	 Product no.:
 Tag no.	FV-3535
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2	inch	Scope: valve body and bonnet
   Rated Cv	50
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	COL reflux to K303	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	11833	10370	7575	l/h	<Note>	Tokumi	V93-9618-	-	59
   Inlet pressure	3.17	3.24	3.24	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	3.05	3.05	3.05	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	4	bar
   Temperature	-182.2	-182.2	-182.2	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	0.739	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	4	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	33.95	23.64	17.27	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	8
 No.:	8	QTY:	1	 Product no.:
 Tag no.	FV-3560
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2	inch	Scope: valve body and bonnet
   Rated Cv	50
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA3	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	Main CH4 purge to Mixer/V311	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	14536	9676	2225	l/h	<Note>	Tokumi	V93-9618-	-	60
   Inlet pressure	2.71	2.73	2.79	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.63	2.67	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	13	bar
   Temperature	-148.3	-148.3	-148.3	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.403	0.403	0.403	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	13	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	43.55	22.45	4.714	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	9
 No.:	9	QTY:	1	 Product no.:
 Tag no.	FV-3715
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/4	inch	Scope: valve body and bonnet
   Rated Cv	14
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA2	      
   Manual operator
   Valve action	DIRECT(Air fail open)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	4.0bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD3D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Open
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	P-301A/B miniflow	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	15323	l/h	<Note>	Tokumi	V93-9618-	-	61
   Inlet pressure	25.53	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.68	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	39	bar	Welded disk
   Temperature	-144.7	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	0.554	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	39	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	2.758	 	Line size  in/out	4	4	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	10
 No.:	10	QTY:	1	 Product no.:
 Tag no.	FV-3725
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/4	inch	Scope: valve body and bonnet
   Rated Cv	14
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA2	      
   Manual operator
   Valve action	DIRECT(Air fail open)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	4.0bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD3D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Open
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	P-301A/B miniflow	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	15323	l/h	<Note>	Tokumi	V93-9618-	-	62
   Inlet pressure	25.53	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.68	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	39	bar	Welded disk
   Temperature	-144.7	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	0.554	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	39	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	2.758	 	Line size  in/out	4	4	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	11
 No.:	11	QTY:	1	 Product no.:
 Tag no.	FV-3883
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1	inch	Scope: valve body and bonnet
   Rated Cv	10
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	HPCOL-2fromE302toV304	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	13614	10246	l/h	<Note>	Tokumi	V93-9618-	-	63
   Inlet pressure	25.4	25.4	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.65	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	34	bar	Welded disk
   Temperature	-180	-180	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	water=1
   	1.25	1.25	kg/m3[N]
   Viscosity	cP
   Flash	3.15	3.16	%	<Line spec>
	Design press.	34	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	3.143	2.366	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	12
 No.:	12	QTY:	1	 Product no.:
 Tag no.	HV-3381
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/2	inch	Scope: valve body and bonnet
   Rated Cv	30
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA4	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	Gas lift for SG5toK-303	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	6000	3000	900	m3/h[N]	<Note>	Tokumi	V93-9618-	-	64
   Inlet pressure	27.07	27.07	27.07	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.85	2.85	2.85	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	34	bar	Welded disk
   Temperature	-139.5	-139.5	-139.5	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	water=1
   	1.25	1.25	1.25	kg/m3[N]
   Viscosity	cP
   Flash	3.15	%	<Line spec>
	Design press.	34	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	10.49	5.246	1.574	 	Line size  in/out	1-1/2	1-1/2	inch
	Line Sch. / Thick.	10S	2.8	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	13
 No.:	13	QTY:	1	 Product no.:
 Tag no.	HV-3428
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1	inch	Scope: valve body and bonnet
   Rated Cv	14
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	SGL1 bypassing E-302	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	8062	1613	l/h	<Note>	Tokumi	V93-9618-	-	65
   Inlet pressure	23.85	23.85	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	8.11	8.11	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	30	bar
   Temperature	-180	-180	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.627	0.629	water=1
   	1	1	kg/m3[N]
   Viscosity	cP
   Flash	3.04	3.57	%	<Line spec>
	Design press.	30	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	2.032	0.4134	 	Line size  in/out	3	1-1/2	inch
	Line Sch. / Thick.	2.77	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	14
 No.:	14	QTY:	1	 Product no.:
 Tag no.	HV-3540
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/2	inch	Scope: valve body and bonnet
   Rated Cv	30
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA3	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	Liquid N2 for startup	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	9578	l/h	<Note>	Tokumi	V93-9618-	-	66
   Inlet pressure	5.5	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	4.2	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	17	bar
   Temperature	-178	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	0.718	water=1
   	1.25	kg/m3[N]
   Viscosity	cP
   Flash	10	%	<Line spec>
	Design press.	17	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	12.79	 	Line size  in/out	1-1/2	1-1/2	inch
	Line Sch. / Thick.	10S	2.77	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	15
 No.:	15	QTY:	1	 Product no.:
 Tag no.	LV-3316
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2-1/2	inch	Scope: valve body and bonnet
   Rated Cv	85
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA3	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	COL LPtoV302	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	31890	29760	18331	l/h	<Note>	Tokumi	V93-9618-	-	67
   Inlet pressure	3.73	3.73	3.73	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.65	2.36	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	4	bar
   Temperature	-182.2	-182.2	-182.2	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	0.739	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	4	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	30.49	28.46	15.56	 	Line size  in/out	6	6	inch
	Line Sch. / Thick.	10S	3.4	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	16
 No.:	16	QTY:	1	 Product no.:
 Tag no.	LV-3420
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2	inch	Scope: valve body and bonnet
   Rated Cv	50
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA4	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	SGL1 from V303toV301	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	32932	26485	6571	l/h	<Note>	Tokumi	V93-9618-	-	68
   Inlet pressure	23.85	23.86	23.85	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	10.82	9.42	7.22	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	30	bar
   Temperature	-180	-180	-180	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.626	0.613	0.630	water=1
   	1	0.98	1	kg/m3[N]
   Viscosity	cP
   Flash	2.98	2.88	3.5	%	<Line spec>
	Design press.	30	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	9.01	6.829	1.642	 	Line size  in/out	6	3	inch
	Line Sch. / Thick.	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	17
 No.:	17	QTY:	1	 Product no.:
 Tag no.	LV-3421
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2	inch	Scope: valve body and bonnet
   Rated Cv	50
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA4	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	SGL from K301toK302	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	40971	40382	26422	l/h	<Note>	Tokumi	V93-9618-	-	69
   Inlet pressure	24.11	24.11	24.13	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	10.18	9.18	6.97	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	30	bar
   Temperature	-177.1	-176.9	-174.8	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.536	0.539	0.51	water=1
   	0.85	0.86	0.82	kg/m3[N]
   Viscosity	cP
   Flash	2.18	2.24	2.29	%	<Line spec>
	Design press.	30	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	9.864	9.458	5.66	 	Line size  in/out	6	4	inch
	Line Sch. / Thick.	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	18
 No.:	18	QTY:	1	 Product no.:
 Tag no.	LV-3422
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1	inch	Scope: valve body and bonnet
   Rated Cv	10
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	HPCOL-5 toV305	[	FLASH	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	7829	7974	3733	l/h	<Note>	Tokumi	V93-9618-	-	70
   Inlet pressure	25.6	25.6	25.6	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.65	2.65	barA	Swagelock double ferules
   Diff. pressure	bar	with Diffuser
   Shut-off press.	34	bar	Welded disk
   Temperature	-178.3	-178.3	-178.3	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.739	0.739	0.739	water=1
   	0.966	0.966	0.966	kg/m3[N]
   Viscosity	cP
   Flash	5.04	5.03	5.04	%	<Line spec>
	Design press.	34	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	1.957	1.993	0.9333	 	Line size  in/out	2	3	inch
	Line Sch. / Thick.	10S	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	19
 No.:	19	QTY:	1	 Product no.:
 Tag no.	LV-3423A
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3	inch	  SV0801-E01    Material certificate in english. 
	   Port size	2	inch	Scope: valve body and bonnet
   Rated Cv	50
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA3	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYQ-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	SGL4 toK303	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	44056	41845	22339	l/h	<Note>	Tokumi	V93-9618-	-	71
   Inlet pressure	7.1	8.09	7.94	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.65	2.65	2.65	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	13	bar
   Temperature	-180	-180	-180	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.572	0.577	0.55	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	13	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	18.26	15.75	8.327	 	Line size  in/out	6	6	inch
	Line Sch. / Thick.	3.4	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	20
 No.:	20	QTY:	1	 Product no.:
 Tag no.	LV-3423B
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/2	inch	Scope: valve body and bonnet
   Rated Cv	30
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	SGL5 toE302	[	LIQUID	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	27190	22583	10794	l/h	<Note>	Tokumi	V93-9618-	-	72
   Inlet pressure	7.99	8.6	8.42	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.8	2.8	2.8	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	13	bar
   Temperature	-180	-180	-180	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	0.594	0.577	0.55	water=1
   	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	13	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	10.63	8.234	3.903	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	3.05	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	21
 No.:	21	QTY:	1	 Product no.:
 Tag no.	PV-3406A
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1	inch	  SV0801-E01    Material certificate in english. 
	   Port size	Cv=10	inch	Scope: valve body and bonnet
   Rated Cv	10
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	PLAIN(BODY EXTENSION)
   Actuator	PSA1	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	FG to Mixer/V311	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	1680	1509	741	m3/h[N]	<Note>	Tokumi	V93-9618-	-	73
   Inlet pressure	8.5	9.1	8.9	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	2.71	2.71	2.71	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	13	bar
   Temperature	-176.5	-176.5	-174.3	degC	STEM AXIS:25 dgrees/Horizontal
   Sp.Gr. (liq.)	water=1
   	0.35	0.34	0.35	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	13	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	4.21	3.482	1.794	 	Line size  in/out	2	2	inch
	Line Sch. / Thick.	2.77	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	22
 No.:	22	QTY:	1	 Product no.:
 Tag no.	PV-3406B
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	4	inch	  SV0801-E01    Material certificate in english. 
	   Port size	4	inch	Scope: valve body and bonnet
   Rated Cv	200
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA6	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	spiral, V563(PTFE)
   Grease
	      
   Air supply	4.0bar
   Spring range	2.0-3.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD3D-1CYL-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	K-302 safety valve bypass	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	15593	m3/h[N]	<Note>	Tokumi	V93-9618-	-	74
   Inlet pressure	12	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	1.2	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	13	bar
   Temperature	-166.6	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	water=1
   	1.25	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	13	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	54.92	 	Line size  in/out	4	6	inch
	Line Sch. / Thick.	3.4	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	23
 No.:	23	QTY:	1	 Product no.:
 Tag no.	PV-3531A
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	HTS
   Description	Top-Guided Single Seated Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	6	inch	  SV0210    High differential pressure trim for 
	   Port size	5	inch	HTS Valve
   Rated Cv	275
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	  SV0801-E01    Material certificate in english. 
   Body material	A351CF8M	Scope: valve body and bonnet
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2W
   Actuator	HA4	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYN-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	K-303 safety valve bypass	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	16899	14088	6765	m3/h[N]	<Note>	Tokumi	V93-9618-	-	79
   Inlet pressure	4	4	4	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	1.2	1.2	1.2	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	4	bar
   Temperature	-150	-150	-150	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	water=1
   	0.96	0.93	0.88	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	4	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	168.2	138	64.48	 	Line size  in/out	6	10	inch
	Line Sch. / Thick.	10S	4	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	24
 No.:	24	QTY:	1	 Product no.:
 Tag no.	SV-3640
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	3	inch	  SV0801-E01    Material certificate in english. 
	   Port size	3	inch	Scope: valve body and bonnet
   Rated Cv	115
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA6	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	4.0bar
   Spring range	2.0-3.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD3D-1CYL-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	ET-301 inlet	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	4738	3635	2850	m3/h[N]	<Note>	Tokumi	V93-9618-	-	75
   Inlet pressure	27.33	27.33	27.33	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	27.14	20.26	16.2	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	34	bar	with Diffuser
   Temperature	11.6	-5.8	5.5	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	water=1
   	1.25	1.25	1.25	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	34	barG
	Design temp.	5.5 ~65	degC
   Calculated Cv	88.15	11.49	7.666	 	Line size  in/out	3	3	inch
	Line Sch. / Thick.	10S	3	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	25
 No.:	25	QTY:	1	 Product no.:
 Tag no.	TDV-3510
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1-1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	1-1/4	inch	Scope: valve body and bonnet
   Rated Cv	21
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA2	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal	AVP302-USD2D-1CYS-X
       Exprosion-proof	CENELEC Intrinsically safe, 1/4 NPT, 1/2 NPT	      
       Signal	4-20 mADC
   Regurator	KZ03-2B-XX
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	Liquid N2to E-304	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	1400	m3/h[N]	<Note>	Tokumi	V93-9618-	-	76
   Inlet pressure	5.5	barA	Air piping: Stainless steel (316ss)
   Outlet pressure	1.27	barA	Swagelock double ferules
   Diff. pressure	bar	Welded disk
   Shut-off press.	17	bar
   Temperature	-178	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	water=1
   	1.25	kg/m3[N]
   Viscosity	cP
   Flash	%	<Line spec>
	Design press.	17	barG
	Design temp.	-196 ~65	degC
   Calculated Cv	10.17	 	Line size  in/out	1-1/2	1-1/2	inch
	Line Sch. / Thick.	10S	2.8	mm
427: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE