Specification Sheet	Page:	1
 No.:	1	QTY:	1	 Product no.:
 Tag no.	HV-3711A
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	HTS
   Description	Top-Guided Single Seated Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	6	inch	  SV0210    High differential pressure trim for 
	   Port size	5	inch	HTS Valve
   Rated Cv	275
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	  SV0801-E01    Material certificate in english. 
   Body material	A351CF8M	Scope: valve body and bonnet
   Trim material	SUS316 STELLITE
   Flow characteristic	LINEAR	      
   Bonnet type	EXTENTION-2W
   Actuator	PSA6	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	5.0bar
   Spring range	2.0-3.9bar
< Accesories >	      
   Positioner / Signal
       Exprosion-proof	      
       Signal	On-Off action
   Regurator	KZ03-3B-1C
   Regulator 2	      
   Limit Switch	P+F(with Terminal box)
        Action	Full Open on	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	CH4 from K-303 to P-301A	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	19500	18950	13200	m3/h[N]	<Note>	Tokumi	V93-9618-	-	80
   Inlet pressure	3	3	3	barA	Air piping: Steinless steel(316ss)
   Outlet pressure	barA	Swagelock double ferules
   Diff. pressure	bar	Welded Disk
   Shut-off press.	3	bar
   Temperature	-148.3	-148.3	-148.3	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	water=1
   	0.72	0.72	0.72	air=1
   Viscosity	cP
   Flash	%	<Line spec>
   Velocity	Mach	Design press.	15	barG
   S.P.L.	dBA	Design temp.	-196 ~65	degC
   Calculated Cv	 	Line size  in/out	6	6	inch
   Travel	%	Line Sch. / Thick.	40S	7.1	mm
426: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	2
 No.:	2	QTY:	1	 Product no.:
 Tag no.	HV-3711B
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	Cv=4.0	inch	Scope: valve body and bonnet
   Rated Cv	4.0
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA1	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal
       Exprosion-proof	      
       Signal	On-Off action
   Regurator	KZ03-2B-1B
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	P-301A/Bblowdown(Cooling 	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	m3/h[N]	<Note>	Tokumi	V93-9618-	-	77
   Inlet pressure	barA	Air piping: Steinless steel(316ss)
   Outlet pressure	barA	Swagelock double ferules
   Diff. pressure	bar	Welded Disk
   Shut-off press.	39	bar	STEM AXIS:Vertical
   Temperature	degC
   Sp.Gr. (liq.)	water=1
   	air=1
   Viscosity	cP
   Flash	%	<Line spec>
   Velocity	Mach	Design press.	39	barG
   S.P.L.	dBA	Design temp.	-196 ~65	degC
   Calculated Cv	 	Line size  in/out	1/2	1/2	inch
   Travel	%	Line Sch. / Thick.	10S	2.1	mm
426: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	3
 No.:	3	QTY:	1	 Product no.:
 Tag no.	HV-3721A
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	HTS
   Description	Top-Guided Single Seated Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	6	inch	  SV0210    High differential pressure trim for 
	   Port size	5	inch	HTS Valve
   Rated Cv	275
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	  SV0801-E01    Material certificate in english. 
   Body material	A351CF8M	Scope: valve body and bonnet
   Trim material	SUS316 STELLITE
   Flow characteristic	LINEAR	      
   Bonnet type	EXTENTION-2W
   Actuator	PSA6	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	5.0bar
   Spring range	2.0-3.9bar
< Accesories >	      
   Positioner / Signal
       Exprosion-proof	      
       Signal	On-Off action
   Regurator	KZ03-3B-1C
   Regulator 2	      
   Limit Switch	P+F(with Terminal box)
        Action	Full Open on	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	CH4 from K-303 to P-301B	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	19500	18950	13200	m3/h[N]	<Note>	Tokumi	V93-9618-	-	81
   Inlet pressure	3	3	3	barA	Air piping: Steinless steel(316ss)
   Outlet pressure	barA	Swagelock double ferules
   Diff. pressure	bar	Welded Disk
   Shut-off press.	3	bar
   Temperature	-148.3	-148.3	-148.3	degC	STEM AXIS:Vertical
   Sp.Gr. (liq.)	water=1
   	0.72	0.72	0.72	air=1
   Viscosity	cP
   Flash	%	<Line spec>
   Velocity	Mach	Design press.	15	barG
   S.P.L.	dBA	Design temp.	-196 ~65	degC
   Calculated Cv	 	Line size  in/out	6	6	inch
   Travel	%	Line Sch. / Thick.	40S	7.1	mm
426: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE

	 Specification Sheet	Page:	4
 No.:	4	QTY:	1	 Product no.:
 Tag no.	HV-3721B
 Service	<Option>
	  SV0703-102    Indicating unit : "bar"
< Specification >
   Model	AGVM
   Description	 Top-Guided Single-Seat Control Valves	  SV0601-001    Air piping Connection: 1/4 NPT
   Valve size	1/2	inch	  SV0801-E01    Material certificate in english. 
	   Port size	Cv=4.0	inch	Scope: valve body and bonnet
   Rated Cv	4.0
   Connection size	inch	  SV0018-005    Oil-free Gr.B (For stainless steel 
   Body rating	ANSI300	body)  and Water-free treatment
   End connection	BW	      
   Body material	A351CF8M
   Trim material	SUS316 STELLITE
   Flow characteristic	EQ%	      
   Bonnet type	EXTENTION-2
   Actuator	PSA1	      
   Manual operator
   Valve action	REVERSE(Air fail close)
   Gland packing	V-PTFE	      
   Gasket	V543(PTFE), V563(PTFE)
   Grease
	      
   Air supply	2.7bar
   Spring range	0.8-2.4bar
< Accesories >	      
   Positioner / Signal
       Exprosion-proof	      
       Signal	On-Off action
   Regurator	KZ03-2B-1B
   Regulator 2	      
   Limit Switch
        Action	      
   Solenoid valve	WBIS 8314 A301
        Action	En. : Control , De-en.: CV Close
        Power supply	DC24V	<Finish>
   Others	     Body:
 	     Diaph. Case:
 	     Yoke:
	     Paint:
<Operating condition>	<Seat Leakage>
   Fluid name	P-301A/Bblowdown(Cooling 	[	GAS	]	CLASS IV-S1 (SV0201-009)
	 	MAX	NOR	MIN	UNIT
   Flow rate	m3/h[N]	<Note>	Tokumi	V93-9618-	-	78
   Inlet pressure	barA	Air piping: Steinless steel(316ss)
   Outlet pressure	barA	Swagelock double ferules
   Diff. pressure	bar	Welded Disk
   Shut-off press.	39	bar	STEM AXIS:Vertical
   Temperature	degC
   Sp.Gr. (liq.)	water=1
   	air=1
   Viscosity	cP
   Flash	%	<Line spec>
   Velocity	Mach	Design press.	39	barG
   S.P.L.	dBA	Design temp.	-196 ~65	degC
   Calculated Cv	 	Line size  in/out	1/2	1/2	inch
   Travel	%	Line Sch. / Thick.	10S	2.1	mm
426: Air Liquide France (Rev.2)/ Caojing 	YAMATAKE