## HIGHLIGHTS
Deviations & Clarifications
HIGHLIGHTS OF THE OFFER
Highlights:
• | We have offered following specifications for your given details:
1) | For Globe Valve,
- | Design Standard is as per ASME B16.34.
- | Face to face dimensions is as per ISA-S 75.
- | Seat Leakage Class IV as per FCI 70.2.
2) | For Ball valve,
- | Design Standard for Trunnion Ball Valve is as per API 6D.
- | Face to face dimensions is as per B 16.32.
- | Seat Leakage Class as per API 598.
3) | Low Fuguitive Emission Packing is as per ISO 15848-2.
4) | Against valve of Tag No.3-FV-1454, 3-LV-1401, 3-LV-1420 & 3-PV-1404, The service application found to be
Flashing. For Flashing application, we have done selection as given below:
a) | Trim Form offered is Contour Ported balance Cage guide.
b) | Flow Direction is Over the plug.
c) | To enhance the trim life, the hard facing of Full Stellite have been provided.
d) | The trims have been offered as reduced port to enhance the life.
5) | Actuator
- | Our Diaphragm Actuator suitable for Minimum supply pressure at 2.4 KG/CM2 & Maximum at 3.0 KG/CM2.
- | For Piston Actuator minimum required supply pressure is 6.0 KG/CM2.
• | We have offered Accessories as followed:
1) | Solenoid valve of Asco make Model No. NF8327B102 ((Ex proof IIC) with Class H Coli & SIL-3 Certified).
2) | Proximity Limit switch with Internal switches of P & F & junction box of Rotex make Model No. DNLF 6A2
((Junction Box Enclosure is Ex proof IIC) with SIL-2 Certified).
• | Painting
- | Painting as per manufacture's standard.
- | Against valve of Tag No.3-XV-1499,we are unable to decode Actuator painting Orange5YR 6.5/11.
Please elaborate
• | Testing
- | For Globe Valve-Radiography test of body and bonnet as per B16.34.
- | Positive Material Identification (PMI) test on Stainless Steel parts.
- | For Globe Valve-Hydro (Shell) test as per ASME B 16.34.
- | For Ball Valve-Hydro (Shell) test as per API 598.
- | For Globe Valve- Material Test cetificates for Body & Bonnet is as per EN10204 3.1 and trim part as per 2.2.
- | For Ball Valve- Material Test cetificates for Body & Side piece is as per EN10204 3.1 and Ball, Seat & Shaft as
per 2.2.
• | Deviations:
1) | According to the following table:
| Item No. | Tag No. | Valve size | Operating Temperature | Design Temperature
| 001 | 3-FV-1454 | 300 mm | 193.4⁰C | 220⁰C
| 002 | 3-LV-1401 | 350 mm | 204.4⁰C | 245⁰C
| 002-Alt | 3-LV-1401 | 300 mm | 204.4⁰C | 245⁰C
| 003 | 3-LV-1420 | 400 mm | 216.2⁰C | 255⁰C
| 003-Alt | 3-LV-1420 | 400 mm | 216.2⁰C | 255⁰C
| 004 | 3-PV-1404 | 350 mm | 234.5⁰C | 280⁰C
| 005 | 3-PV-1436 | 450 mm | 224⁰C | 300⁰C
| 005-Alt | 3-PV-1436 | 450 mm | 224⁰C | 300⁰C
| 006 | 3-XV-1499 | 250 mm | 227⁰C | 300⁰C
Also the operating temperature are higher than 210⁰c, we have offered PEEK seat for Tag numbers indicated in
above table. The maximum temperature limit for PEEK is 265°C. The operating temperature of all above tag are
well below 234.5°C. however for tag no. 3-PV-1404, 3-PV-1436 & 3-XV-1499. design temperature are higher.
Please look into this matter. Confirm us wheather PEEK is acceptable.
2) | Against valve of Tag No. 3-PV-1404 & 3-PV-1436, Due to higher thrust values we have offered valve with piston
cylinder actuator instead of Diaphragm actuator.
3) | Against valve of Tag No.3-XV-1499, Minimum stoke time of valve will be 6 to 7 secs instead of 1 sec.

## 6
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 6 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-FV-1454
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 350 mm/ 350 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Ethylene glycol/Water |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 261700 | 218144 | 109072 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 11.21 | 11.22 | 11.22 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 4.1073 | 4.1113 | 4.1063 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 7.104 | 7.11 | 7.115 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 193.4 | 193.4 | 193.4 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0.8866 | 0.8866 | 0.8866 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 12.23 | 12.23 | 12.23
| 10 | Critical Pressure |  | Kg/cm2A | 225.6 | 225.6 | 225.6 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0.169 | 0.169 | 0.169 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 317.762 | 263.772 | 131.811 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 640 | 640 | 640 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 74 | 69 | 54 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 77.4802 | 76.6938 | 73.7086
| 18 | Final Noise Level |  | dBA | 77.4802 | 76.6938 | 73.7086 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 15 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 300 mm ¦ 200 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | CONTOUR PORTED BALANCE CAGE GUIDE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 316 FSF |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 316 FSF + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 316 FSF |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | OVER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | DIAPHRAGM ¦ REVERSE ACTING |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 0.4-2.0 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 2.4 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RMp-44-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 1/2" NPT
| 42 | Hand Wheel |  |  | NO
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B7/2H
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 15 Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 220⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 9
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 9 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-LV-1401
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 450 mm/ 450 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Ethylene glycol/Water |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 401500 | 334557 | 167278 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 15.23 | 15.23 | 15.23 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 11.4746 | 11.4716 | 11.4686 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 3.759 | 3.762 | 3.765 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 204.4 | 204.4 | 204.4 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0.8686 | 0.8686 | 0.8686 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 16.23 | 16.23 | 16.23
| 10 | Critical Pressure |  | Kg/cm2A | 225.6 | 225.6 | 225.6 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0.146 | 0.146 | 0.146 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 405.454 | 337.715 | 168.741 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 640 | 640 | 640 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 79 | 75 | 59 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 49.6276 | 48.8532 | 45.8607
| 18 | Final Noise Level |  | dBA | 49.6276 | 48.8532 | 45.8607 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 20.5 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 350 mm ¦ 200 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | CONTOUR PORTED BALANCE CAGE GUIDE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 316 FSF |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 316 FSF + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 316 FSF |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | OVER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | DIAPHRAGM ¦ REVERSE ACTING |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 0.6-2.2 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 2.6 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RMp-44-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 3/8" NPT
| 42 | Hand Wheel |  |  | SIDE MOUNTED
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B7/2H
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 20.5 Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 245⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 9-ALT
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 9 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-LV-1401(Alternative)
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 450 mm/ 450 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Ethylene glycol/Water |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 401500 | 334557 | 167278 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 15.23 | 15.23 | 15.23 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 11.4746 | 11.4716 | 11.4686 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 3.759 | 3.762 | 3.765 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 204.4 | 204.4 | 204.4 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0.8686 | 0.8686 | 0.8686 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 16.23 | 16.23 | 16.23
| 10 | Critical Pressure |  | Kg/cm2A | 225.6 | 225.6 | 225.6 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0.146 | 0.146 | 0.146 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 406.174 | 339.233 | 169.498 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 640 | 640 | 640 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 79 | 75 | 59 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 49.6448 | 48.8704 | 45.8778
| 18 | Final Noise Level |  | dBA | 49.6448 | 48.8704 | 45.8778 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 20.5 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 300 mm ¦ 200 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | CONTOUR PORTED BALANCE CAGE GUIDE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 316 FSF |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 316 FSF + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 316 FSF |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | OVER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | DIAPHRAGM ¦ REVERSE ACTING |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 0.6-2.2 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 2.6 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RMp-44-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 3/8" NPT
| 42 | Hand Wheel |  |  | SIDE MOUNTED
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B7/2H
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 20.5 Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 245⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 11
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 11 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-LV-1420
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 500 mm/ 500 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Ethylene glycol/Water |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 534200 | 445210 | 222605 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 19.93 | 19.93 | 19.93 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 15.3558 | 15.3488 | 15.3348 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 4.579 | 4.586 | 4.6 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 216.2 | 216.2 | 216.2 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0.852 | 0.852 | 0.852 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 20.93 | 20.93 | 20.93
| 10 | Critical Pressure |  | Kg/cm2A | 225.6 | 225.6 | 225.6 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0.133 | 0.133 | 0.133 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 459.995 | 383.258 | 191.536 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 640 | 640 | 640 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 82 | 78 | 62 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 49.182 | 48.4242 | 45.4811
| 18 | Final Noise Level |  | dBA | 49.182 | 48.4242 | 45.4811 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 23.5 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 400 mm ¦ 200 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | CONTOUR PORTED BALANCE CAGE GUIDE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 316 FSF |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 316 FSF + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 316 FSF |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | OVER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | DIAPHRAGM ¦ REVERSE ACTING |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 0.6-2.2 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 2.6 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RMp-44-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 1/2"NPT
| 42 | Hand Wheel |  |  | SIDE MOUNTED
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B 8M/8M
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 23.5 Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 255⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 11-ALT
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 11 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-LV-1420 (Alternative)
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 500 mm/ 500 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Ethylene glycol/Water |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 534200 | 445210 | 222605 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 19.93 | 19.93 | 19.93 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 15.3558 | 15.3488 | 15.3348 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 4.579 | 4.586 | 4.6 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 216.2 | 216.2 | 216.2 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0.852 | 0.852 | 0.852 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 20.93 | 20.93 | 20.93
| 10 | Critical Pressure |  | Kg/cm2A | 225.6 | 225.6 | 225.6 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0.133 | 0.133 | 0.133 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 461.559 | 385.559 | 192.685 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 640 | 640 | 640 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 82 | 78 | 62 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 49.25 | 48.4922 | 45.549
| 18 | Final Noise Level |  | dBA | 49.25 | 48.4922 | 45.549 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 23.5 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 300 mm ¦ 200 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | CONTOUR PORTED BALANCE CAGE GUIDE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 316 FSF |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 316 FSF + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 316 FSF |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | OVER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | DIAPHRAGM ¦ REVERSE ACTING |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 0.6-2.2 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 2.6 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RMp-44-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 1/2"NPT
| 42 | Hand Wheel |  |  | SIDE MOUNTED
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B 8M/8M
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 23.5 Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 255⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 15
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 15 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-PV-1404
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 350 mm/ 350 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Ethylene glycol/Water |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 656300 | 546925 | 273462 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 34.09 | 34.14 | 34.23 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 19.7562 | 19.7562 | 19.7462 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 14.34 | 14.39 | 14.49 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 234.5 | 234.5 | 234.5 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0.1823 | 0.1823 | 0.1823 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 29.83 | 29.83 | 29.83
| 10 | Critical Pressure |  | Kg/cm2A | 225.6 | 225.6 | 225.6 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0.12 | 0.12 | 0.12 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 642.69 | 534.18 | 265.84 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 1000 | 1000 | 1000 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 80 | 75 | 59 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 78.8437 | 78.0746 | 75.1095
| 18 | Final Noise Level |  | dBA | 78.8437 | 78.0746 | 75.1095 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 55.6 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 350 mm ¦ 250 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 600# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 351 GR. CF8M |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | CONTOUR PORTED BALANCE CAGE GUIDE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 316 FSF |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 316 FSF + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 316 FSF |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | OVER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | LINEAR PISTON S/A |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 2.0-4.0 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 6.0 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RPM-400-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 1/2" NPT
| 42 | Hand Wheel |  |  | SIDE MOUNTED
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B 8M/8M
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 55.6Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 280⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 16
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 16 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-PV-1436
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 450 mm/ 450 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Steam |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 115000 | 95818 | 47909 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 24.47 | 24.58 | 24.68 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 23.4574 | 23.5674 | 23.6674 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 1.02 | 1.02 | 1.02 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 224 | 224 | 224 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0 | 0 | 0 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A
| 10 | Critical Pressure |  | Kg/cm2A | 0 | 0 | 0 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0 | 0 | 0 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 1188.9854 | 988.4897 | 493.2633 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 1950 | 1950 | 1950 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 79 | 74 | 58 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 86.6608 | 85.8969 | 82.9125
| 18 | Final Noise Level |  | dBA | 71.6608 | 70.8969 | 67.9125 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 27.5 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 450 mm ¦ 400 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | M. H. CAGE BALANCE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 431 HTH |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 431 HTH + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 431 HTH |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | UNDER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL+ LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | LINEAR PISTION D/A |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | ----------- |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 4.0 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | PD-300-178
| 40 | Valve Travel |  |  | 178 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 1/2" NPT
| 42 | Hand Wheel |  |  | NO | [5 empty] | Air Fail Back-up System | Air Fail Back-up System with Tank
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B7/2H
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 27.5Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 300⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark | 1) VALVE WITH VOLUME TANK ARRANGEMENT.

## 16-ALT
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 16 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-PV-1436(Alternative)
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 450 mm/ 450 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Steam |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 115000 | 95818 | 47909 |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 24.47 | 24.58 | 24.68 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 23.4574 | 23.5674 | 23.6674 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 1.02 | 1.02 | 1.02 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 224 | 224 | 224 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0 | 0 | 0 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 0 | 0 | 0
| 10 | Critical Pressure |  | Kg/cm2A | 0 | 0 | 0 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise | 0 | 0 | 0 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 1191.7086 | 990.7537 | 494.3931 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 1950 | 1950 | 1950 |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | EQ.% |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 79 | 74 | 58 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 86.6707 | 85.9068 | 82.9224
| 18 | Final Noise Level |  | dBA | 71.6707 | 70.9068 | 67.9224 |  | Solenoid Valve | 70 | Model No.
| 19 | Max Shut Off Dp |  | Kg/cm2 | 27.5 | 0 | 0 |  |  | 71 | Make
Body & Trim | 20 | Dembla Series |  |  | 1100 |  |  |  |  | 72 | Type
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection
| 22 | Body Form |  |  | GLOBE SINGLE SEAT |  |  |  |  | 74 | Cable Entry & Enclosure
| 23 | Size Body / Size Trim |  |  | 400 mm ¦ 400 mm |  |  |  |  | 75 | Body Moc.
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override
| 27 | Trim Form |  |  | M. H. CAGE BALANCE |  |  |  | Limit Switch
| 28 | Trim Material | Plug/ Disc/ Ball ¦ Facing |  | SS 431 HTH |  |  |  |  | 79 | Model No
|  |  | Seat Ring ¦ Facing |  | SS 431 HTH + PEEK |  |  |  |  | 80 | Quantity
|  |  | Guide /Large Guide | [6 empty] | 81 | Make
|  |  | Cage /Seat Retainer |  | SS 431 HTH |  |  |  |  | 82 | Type
|  |  | Seal Ring | [6 empty] | 83 | Contacts
| 29 | Flow Direction |  |  | UNDER THE PLUG |  |  |  |  | 84 | Current Rating
| 30 | Seat Leakage(FCI 70.2) |  |  | CLASS IV |  |  |  |  | 85 | Housing Moc.
| 31 | Bonnet Type |  |  | EXTENDED FINNED |  |  |  |  | 86 | Enclosure
| 32 | Gland Packing |  |  | GRAFOIL+ LFE |  |  |  |  | 87 | Mounting Position
Actuator | 33 | Actuator Type ¦ Action |  |  | LINEAR PISTON S/A |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | 2.0-4.0 KG/CM2 |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 6.0 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | RPM-400-108
| 40 | Valve Travel |  |  | 108 mm
| 41 | Size(inch)² ¦ Supply Connection |  |  | 250 ¦ 1/2" NPT
| 42 | Hand Wheel |  |  | NO
Positioner | 43 | Model No. |  |  | AVP302-C
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol
| 45 | Make |  |  | AZBIL corporation
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B7/2H
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 27.5Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 300⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark

## 17
DOCUMENT NO :
CUSTOMER |  |  | SHARQ EG3 |  |  |  |  | PLACE |  |  | Saudi Arabia
YOUR REF | [7 empty] | DATE
OUR REF | [7 empty] | DATE |  |  | 2012-10-22
ITEM NO |  |  | 17 |  |  |  |  | QUANTITY |  |  | 1 No
TAG NO |  |  | 3-XV-1499
SERVICE APPLICATION
PIPE LINE IN./OUT/SCH |  |  |  | 250 mm/ 250 mm/ Schedule 40
Service Condition | 1 | Fluid |  | Steam |  |  |  |  | I/P Convertor | 54 | Model No.
|  |  |  | Unit | Max | Nor | Min |  |  | 55 | Make
| 2 | Flow |  | Kg/hr | 0 | 0 |  |  |  | 56 | Input Signal
| 3 | Inlet Pressure |  | Kg/cm2 | 0 | 0 | 0 |  |  | 57 | Output Signal
| 4 | Outlet Pressure |  | Kg/cm2 | 0 | 0 | 0 |  |  | 58 | Pnu. Conn.
| 5 | DP Valve Sizing |  | Kg/cm2 | 0 | 0 | 0 |  |  | 59 | Cable Entry
| 6 | Inlet Temperature |  | deg. C | 227 | 0 | 0 |  |  | 60 | Supply
| 7 | Sp. Gravity |  |  | 0 | 0 | 0 |  |  | 61 | Hsg. Material
| 8 | MW |  |  | 0 | 0 | 0 |  |  | 62 | Enclosure
| 9 | Vapour Pressure |  | Kg/cm2A | 0 | 0 | 0
| 10 | Critical Pressure |  | Kg/cm2A | 0 | 0 | 0 |  | Air Set | 63 | Model No. | KZ03-2B-XX
| 11 | Critical Temperature |  | deg. C | 0 | 0 | 0 |  |  | 64 | Quantity | 1 pc
| 12 | Viscosity Cp |  | Centipoise |  | 0 | 0 |  |  | 65 | Make | AZBIL Corporation
| 13 | Corrected Cv |  | Usgpm | 0 | 0 | 0 |  |  | 66 | Pnu. Conn. | 1/4 NPT (F) screw.
| 14 | Selected Cv @ |  | Usgpm | 5000 |  |  |  |  | 67 | Gauge
| 15 | Flow Characteristics |  |  | ON - OFF |  |  |  |  | 68 | Body Moc.
| 16 | Percentage Valve Opening |  |  | 0 | 0 | 0 |  |  | 69 | Filter Size
| 17 | Predicted Noise Level |  | dBA | 0 | 0 | 0
| 18 | Final Noise Level |  | dBA | 0 | 0 | 0 |  | Solenoid Valve | 70 | Model No. | NF8327B102
| 19 | Max Shut Off Dp |  | Kg/cm2 | 25.49 | 0 | 0 |  |  | 71 | Make | ASCO
Body & Trim | 20 | Dembla Series |  |  | 8200 F31 |  |  |  |  | 72 | Type | 3/2 Way
| 21 | Model No. | [7 empty] | 73 | Pnu.Connection | 1/4"NPT[F]
| 22 | Body Form |  |  | `O` BALL VALVE |  |  |  |  | 74 | Cable Entry & Enclosure | 1/2"NPT & Ex proof IIC
| 23 | Size Body / Size Trim |  |  | 250 mm ¦ 250 mm |  |  |  |  | 75 | Body Moc. | SS 316
| 24 | End Connections / Rating | Rating |  | FLANGED R.F. ¦ 300# |  |  |  |  | 76 | Voltage | 24 VDC
| 25 | Body Material |  |  | A 216 GR. WCB |  |  |  |  | 77 | Ins. Class | H (SIL-3 Certified)
| 26 | IBR Certification |  |  | Not Reqd. |  |  |  |  | 78 | Man Override | Nil
| 27 | Trim Form |  |  | `O` BALL |  |  |  | Limit Switch
| 28 | Trim Material | Ball |  | SS 316 |  |  |  |  | 79 | Model No | DNLF 6A2
|  |  | Seat |  | PEEK + SS 316 |  |  |  |  | 80 | Quantity | 2 NO.
|  |  | Shaft |  | A 182 GR. F316 |  |  |  |  | 81 | Make | Internal switches of P & F make with Housing box of Rotex
[10 empty] | 82 | Type | PROXIMITY
[10 empty] | 83 | Contacts | NON-CONTACT
| 29 | Flow Direction |  |  | BIDIRECTION |  |  |  |  | 84 | Current Rating | 8VDC
| 30 | Seat Leakage(FCI 70.2) |  |  | AS PER API 598 |  |  |  |  | 85 | Housing Moc. | SS 316
| 31 | Bonnet Type |  |  | EXTENDED |  |  |  |  | 86 | Junction Box Enclosure | EXPROOF IIC
| 32 | Gland Packing |  |  | GRAFOIL + LFE |  |  |  |  | 87 | Mounting Position | NAMUR (SIL-2 Certified)
Actuator | 33 | Actuator Type ¦ Action |  |  | PISTON CYLINDER S/A |  |  |  | C/F Flanges
| 34 | Valve Action Air Or Power To |  |  | OPEN |  |  |  |  | 88 | Quantity
| 35 | Fail Safe Condition |  |  | FAIL TO CLOSE |  |  |  |  | 89 | Type
| 36 | [8 empty] | 90 | Moc
| 37 | Spring Range |  |  | SPRING RETURN |  |  |  |  | 91 | IBR
| 38 | Supply |  |  | 6.0 KG/CM2 |  |  |  |  | 92 | Rating
| 39 | Actuator Model |  |  | LPS-550-200-90⁰ | [5 empty] | To Achieve Stroke Time (6-7 secs)
| 40 | Valve Travel |  |  | 0-90⁰ | [5 empty] | AFR
| 41 | Size(inch)² ¦ Supply Connection |  |  | 1/2" NPT | [5 empty] | Supply Connection/ Body Moc. | 1/2" NPT / Aluminium
| 42 | Hand Wheel |  |  | No | [5 empty] | Volume Booster
Positioner | 43 | Model No. |  |  | AVP302-C | [5 empty] | Supply Connection/ Body Moc. | 3/4" NPT / Aluminium
| 44 | Positioner Type |  |  | ATEX Flameproof / HART protocol | [5 empty] | Quick Exhaust valve
| 45 | Make |  |  | AZBIL corporation | [5 empty] | Supply Connection/ Body Moc. | 3/4" NPT / Aluminium
| 46 | Action |  |  | Direct
| 47 | By Pass. / No of Gauges |  |  | With By Pass / 2 pcs of Gauge
| 48 | Input Signal |  |  | 4 - 20 mA | [5 empty] | Actuator Colour | Orange
| 49 | Output Signal | [8 empty] | Nuts & Bolts | A 193 GR. B7/2H
| 50 | Supply Pressure | [8 empty] | Gasket | SS 316 sprial wound Graphite filled
| 51 | Pnu.Conn | [8 empty] | Design Pressure | 27.5Bar
| 52 | Cable Entry | [8 empty] | Design Temperature | 300⁰C
| 53 | Enclosure | [8 empty] | Tubing,Fittings | SS 316
Remark