DMC50
Module Type Controller
No.CP—PC—1372E
Multiple functions for free customization
gives you the ultimate in module type controllers
Multiple functions for free customization
gives you the ultimate in module type controllers
Instrumentaion
Converters
Sensors
Controllers
Actuators
Recorders
Systemization
Advanced process control, space saving and flexible networking are all realized.
Process control is evolving as controller designs progress.
The control market has been demanding a general-purpose controller which can
handle advanced process control and
that can flexibly respond to a diversifying network.
The DMC50 incorporates a completely new concept in
controllers that has been developed to meet such customer demands.
This new DMC50 is a next generation, multiple advanced PID controller featuring
the high accuracy, high stability and superior response that Yamatake is known for,
and has multiple operation functions capable of freely constructing process logic.
The DMC50 is also flexible enough to support the ever-diversifying network and
gives the user great freedom over advanced process control.
The input and output signals necessary for responding to advanced
process control are included.
Signal input and output required for
process control included (Control module)
Analog process designing made easily
A RS-485 modular jack is provided on the front panel of the control
module. Direct connection with a Yamatake touch panel enables a
wide variety of applications.
Functions for indication and setting units can be easily realized.
The gateway function eases the programming load of the conversion of data
between the PLC and the DMC50.
Wide variety of applications can be designed
in combination with Yamatake touch panel.
Two communication modules are available for the DMC50 to respond
to wide variety of networks.
DMC50ME200 can execute data communications to a host station
through Ethernet.
DMC50ME200: Ethernet + RS-485 (double host support)
DMC50MR200: RS-485 (single host support, economical)
Flexible communication modules capable of
responding to a range of networks The DMC50 is ideal for designing a control system that meets process
requirements including direct heating characteristics, heat retention
characteristics, and disturbance characteristics. With the incorporation
of the highly accurate control algorithm “Ra-PID”, enhanced
the stability and overshoot suppression functions offering stable control,
which were previously unavailable, are now a reality.
Stable control achieved by
incorporation of new algorithm
The DMC50 can achieve the high
accuracy control of 0.05 to 0.1%FS.
Input sampling cycle is 50ms which is
fast enough to respond to advanced
process control.
High accuracy and high response
New tuning algorithm adopted
Input sampling
50ms
0.05 to 0.1%FS
high accuracy
Control
module
EST240Z
PLC
RS-485 Gateway function
Control module
DMC50
Full-multi input: 4 points
Voltage input: 8 points (max.)
Communication
module
DMC50MR200
Control
module
Max. 8 control modules
EST240Z
RS-485
Analog input
4 to 20mA / 1 to 5Vdc: 4 points
Time proportional current output
Analog output
Transistor output: 16 points
Digital output
Photo-coupler input: 12 points
Digital input
DMC50MR200
RS-485
DMC50ME200
Ethenet+RS-485
Host – 1
Ethernet communications RS-485
Host – 2
RS-485
Host – 3
RS-485
One Yamatake touch panel can exchange data with maximum 8 control
modules if connected with a communication module (DMC50MR200).
DMC50CH400/200
Basic accuracy: ±0.05 to 0.1%FS
High resolution type Special type
DMC50CS400/200
16.000 to 37.000°C: ±0.1°C Effective resolution: 0.0002°C
2
types
Highly accurate control logic
for direct heating systems
Ra-PID
Further advanced high speed
balancing logic of Ra-PID
Just-FiTTER
(Before adoption)
900 1000 1100 1200 1300
Time(sec)
1400 1500 1600
19.98
19.985
20.005
20.01
20.015
20.02
19.99
19.995
20
PV
Control Simulation
900 1000 1100 1200 1300 1400 1500 1600
19.98
19.985
20.005
20.01
20.015
20.02
19.99
19.995
20
Control Simulation
(After adoption) Time(sec)
PV
Control Simulation
(Before adoption) Time(sec)
PV
500 550 600 650 700
30.4
30.3
30.2
30.1
30
29.9
29.8
29.7
29.6
29.5
Control Simulation
(After adoption) Time(sec)
PV
500 550 600 650 700
30.4
30.3
30.2
30.1
30
29.9
29.8
29.7
29.6
29.5
A new concept in module type controllers brings to you
advanced equipment controlling in a familiar, easy-to-use format.
The DMC50 provides a development environment, which enables
the user to freely design a custom advanced control process.
Operation type: 100 types are available including mathematical functions, statistics, logic, time and control.
Operation contents: More than 8 loop operations are possible by switching PID operation contents.
One can select optimum language for describing advanced process programs.
Highly efficient for program development and reutilization of programs.
Specifications
General specifications
Control module
Communication module
Smart loader package
Selection Guide
40.7
(181) (45)
(49.5)
(58.5)
(65)
38.5
(47)
77.2 69.9
Holes for screw mounting
54±0.15
(For M3 screw)
117.3±0.2
(Shortest distance to duct)
65
7.6
2.5
54
47
(60)
(70)
(80)
(90)
145.1
7.5
148
169.5
12.2
8.4
Terminal block
Space for mounting to
terminal block
Space for mounting
to DIN rail
Holes for screw mounting
(For M3 screw)
Body Base
(54)
27
Individual specifications of control modules
Module type
Type
Basic model No.
Power supply
Basic conditions
Operating
conditions
Max. number of connectable units
Mounting
Weight
Rated voltage
Max. consumption current
Ambient temperature
Ambient humidity
Power supply
Ambient temperature
Ambient temperature for guaranteed accuracy
Ambient humidity
Communication module Control module
Ethernet type
DMC50ME200
RS-485 type
DMC50MR200
High resolution (2/4 loops) type
DMC50CH200/400
Special (2/4 loops) type
DMC50CS200/400
21.6 to 26.4Vdc
23±2°C
60±5%RH (no condensation allowed)
24Vdc±2%
0 to 50°C
20 to 90%RH (no condensation allowed)
Max. 8 units of control modules connectable for one communication module
DIN rail mounting or screw mounting
600g max.
0.2A 0.6A
— 0 to 50°C 10 to 40°C
(unit:mm)
Model No.
Model
Analog input
Digital input
Auxiliary input
Analog output
Digital output
No. of input
Input type
Input accuracy
Input sampling cycle
Cold junction compensation accuracy
Cold junction compensation method
Influence of
wiring resistance
No. of input
Input type
Input voltage
Connectable output mode
No. of input
Input type
No. of output
Output type
No. of output
Output mode
DMC50CH200 DMC50CH400 DMC50CS200 DMC50CS400
High function model Special model
Multi-range of T/C, RTD, linear voltage and linear current Multi-range of RTD (dedicated to 4-wire type) and linear voltage
CA: –200.0 to +1200.00°C Accuracy ±0.7°C
Pt100: –60.00 to +100.00°C Accuracy ±0.15°C
Linear: 4 to 20mA Accuracy ±0.05°C
Pt100: 16.000 to 37.000°C Accuracy±0.1°C
RTD input: 0.01%FS/. max.
(within 0 to 10. range of wiring resistance),
Allowable wiring resistance:10. max.
RTD input: 0.01%FS/. max.
(within 0 to 10. range of wiring resistance),
Allowable wiring resistance:1. max.
4 to 8 2 to 4 4 2
12
2
4
16
6
1
2
8
12
2
4
16
6
1
2
8
(Refer to specification
sheets for further
details)
50ms min
±0.7°C (under standard conditions)
Selectable from the following: •Compensation in controller •Compensation in outside of controller (0°C only)
Photo-coupler (bidirectional)
24Vdc±10%
No-voltage contact (relay contact) and open collector
0 to 5Vac, 0 to 6Vac, 0 to 10Vac, 0 to 12Vac, –1 to +6Vdc selectable by setting
Linear output (0 to 20mAdc, 4 to 20mAdc, 0 to 10Vdc) and time proportional current output selectable
Open drain type FET output
Basic model No. Module Additional processing Special processsing
DMC50
CH200
CH400
CS200
CS400
0
T
K
D
B
L
0
Y
0000
Module type controller
High resolution model 2 loops
High resolution model 4 loops
Special model 2 loops
Special model 4 loops
No additional treatment
Tropicalization
Antisulfide treatment
With inspection certificate
Tropicalization with inspection certificate
Antisulfide treatment with inspection certificate
Without traceability certificate
With traceability certificate
(None)
Description
DMC50
MR200
ME200
0
T
K
D
B
L
0
Y
0000
Module type controller
RS-485 1 channe
Ethernet + RS-485 2 channels
No additional treatment
Tropicalization
Antisulfide treatment
With inspection certificate
Tropicalization with inspection certificate
Antisulfide treatment with inspection certificate
Without traceability certificate
With traceability certificate
(None)
SLP-D50
E50
Personal computer loader for DMC50 (CD-ROM)
English version, with a dedicated cable
Description
Dimensions
Yamatake Corporation
Control Products Division
Head office:Totate International Building
2-12-19 Shibuya Shibuya-ku Tokyo 150-8316 Japan
Inquiries to:International Business Division
Phone:81-3-3486-2331, Fax:81-3-3486-2300 (Sales)
Phone:81-466-27-2307, Fax:81-466-27-9264 (Customer Service)
URL:http://www.yamatake.com
Savemation
Saving through Automation
Printed in Japan.(SZ)
Issued Feb.2002
ISaGRAF® is a registered trademark of AlterSys
Specifications are subject to change without notice.
This has been printed on 100% recycled paper.
Basic model No. Module Additional processing Special processsing
Basic model No. Others
Description
Wiring duct