## Tabelle1
Sensor: |  | SS 20.650
Supply voltage: |  | rated value | 24 | V DC
|  | tolerance: | -20 | %
|  | min. value: USupply,min | 19.2 | V DC
Supply current: |  | max. value: ISupply,max | 140 | mA
Operating temperature: |  | TElectronics,max = | 70 | °C |  | Admissible voltage drop over both supply leads:
Typical supply unit: |  | rated value | 24 | V DC |  |  | 2.4 | V
|  | tolerance: | -10 | %
|  | min. value: USupply,min | 21.6 | V DC
Connection cable: |  | Length: | 200 | m
1.) | SCHMIDT cable: | Cross section area | 0.25 | mm2
|  | Resistance per length | 70 | W/km @ TN = | 25 | °C
|  |  | 82.6 | W/km @ Telectronics, max
|  | Max. Voltage drop per supply lead: | 2.3128 | V
|  | Max. Voltage drop over both supply leads: | 4.6256 | V |  | Not admissible!
2.) | Cable AWG22: | Cross section area | 0.34 | mm2
|  | Resistance per length | 52.3 | W/km @ TN = | 25 | °C
|  |  | 61.714 | W/km @ Telectronics, max
|  | Max. Voltage drop per supply lead: | 1.728 | V
|  | Max. Voltage drop over both supply leads: | 3.456 | V |  | Not admissible!
3.) | Cable AWG20: | Cross section area | 0.5 | mm2
|  | Resistance per length | 33 | W/km @ TN = | 25 | °C
|  |  | 38.94 | W/km @ Telectronics, max
|  | Max. Voltage drop per supply lead: | 1.0903 | V
|  | Max. Voltage drop over both supply leads: | 2.1806 | V |  | Admissible!